## Notes
Column Headers for LOOP Event List
LER | The LER number describing the LOOP Event.
Plant Name | The name of the plant that experienced the LOOP event.
Date | The date of the LOOP event.
Operating Mode | Power-Ops or Critical | The LOOP event caused a plant trip during power operation.
| Shutdown | The LOOP event occurred during plant hot or cold shutdown or during plant startup. The Decay Heat mode defined in NUREG/CR-6890 (the plant is at a significant decay-heat point after the scram or shutdown, and it is not able to put a low-pressure shutdown cooling system online) is included in the Shutdown mode in this study.
LOOP Category | GR (grid-related) | A LOOP event in which the initial failure occurs in the interconnected transmission grid that is outside the direct control of plant personnel. Failures that involve transmission lines within the site switchyard are usually classified as switchyard-centered events if plant personnel can take actions to restore power when the fault is cleared. However, the event should be classified as grid related if the transmission lines fail from voltage or frequency instabilities, overload, or other causes that require restoration efforts or corrective action by the transmission operator.
| PC (plant-centered) | A LOOP event in which the design and operational characteristics of the NPP unit itself play the major role in the LOOP cause and duration. Plant-centered failures typically involve hardware failures, design deficiencies, human errors, and localized weather-induced faults such as lightning. The line of demarcation between plant-centered and switchyard-centered events is the NPP main and station power transformers’ high-voltage terminals.
| SC (switchyard-centered) | A LOOP event in which the equipment (or human-induced failures of equipment) in the switchyard plays the major role in the loss-of-offsite power. Switchyard-centered failures typically involve hardware failures, design deficiencies, human errors, and localized weather-induced faults such as lightning. The line of demarcation between switchyard-related events and grid-related events is the point where the transmission lines leave the switchyard.
| WR (weather-related) | A LOOP event caused by severe or extreme weather. Severe weather is defined to be weather with forceful and broad (beyond local) effects. An example is storm damage to transmission lines instead of just debris blown into a transformer. This does not mean that the event had to result in widespread damage, just that the potential existed. Examples of severe weather include thunderstorms, snow, and ice storms. Lightning strikes, though forceful, are normally localized to one unit, and so are coded as plant-centered or switchyard-centered. Extreme weather is distinguished from severe weather by its potential to cause significant damage to the electrical transmission system and long offsite-power restoration times. Examples of extreme weather are hurricanes, strong winds greater than 125 miles per hour, and tornadoes.
LOOP Class | LOOP-IE-I | A LOOP initiating event (LOOP-IE) in which the LOOP event causes the reactor to trip. It is also called initial plant fault LOOP-IE. LOOP-IE-I is a subset of LOOP-IE events. LOOP-IE is defined as a LOOP occurring while a plant is at power and involving a reactor trip. A LOOP occurring while a plant is at power but not involving a reactor trip is called LOOP no-trip event (LOOP-NT), which is not included in the analysis.
| LOOP-IE-C | A consequential LOOP-IE in which the LOOP is the direct or indirect result of a plant trip.
| LOOP-IE-NC | A nonconsequential LOOP-IE in which the LOOP occurs following, but is not related to, the reactor trip.
| LOOP-SD | A LOOP shutdown event when the LOOP occurs during the plant shutdown.
Restoration Time | Actual Bus Restoration Time | The duration, in minutes, from event initiation until offsite electrical power is restored to a safety bus. This is the actual time taken from the onset of the LOOP (time zero) until offsite power is restored from the first available source to a safety bus.
| Potential Bus Recovery Time | The duration from the event initiation until offsite electrical power could have been recovered to a safety bus. This estimated time is less than or equal to the actual bus restoration time. The determination of potential bus recovery time is based on engineering judgement (see Subsection 6.7 of NUREG/CR 6890).
| Switchyard Restoration Time | The duration from event initiation until offsite electrical power is restored (or could have been restored, whichever time is shorter) to the switchyard.
Cause (Note 1) | EEE | Extreme external events: hurricane, winds ≥ 125 mph, tornado, earthquake ≥ R7, flooding ≥ 500-year flood for the site, sabotage
| EQUIP | Hardware related failures
| G | Interconnected grid transmission line events, outside direct plant control
| HE | Human error during any operating mode
| HES | Human error during any shutdown mode
| SEE | Severe external events: lightening, high winds (< 125 mph), snow and ice, salt spray, dust contamination, fires and smoke contamination, earthquake < R7, flooding < 500-year flood for the site
Note 1: It should be noted the differences between the LOOP category and LOOP cause. Depending on whether the hazard impact is localized or widespread and where the induced fault is, a natural hazard caused LOOP event could be coded into a different LOOP category (e.g., LOOP-PC, LOOP-SC, or LOOP-GR) other than LOOP-WR. This is more so for lightning than other nature hazards such as hurricanes and tornadoes due to the typically localized impacts from lightning.
A specific cause is based on the selection of the Cause. Specific causes are listed below.
Cause | Specific Cause | Specific Cause Description
EEE | Earthquake ≥ 7.0 | Earthquake ≥ 7.0 on the Richter Scale
| Flooding ≥ 500 year | Flooding ≥ 500-year flood for the site
| Hurricane | Hurricane, Winds ≥ 125 mph
| Tornado | Tornado
EQUIP | Breaker | Direct circuit breaker failure or failure of controls specific to one circuit breaker
| Circuits | Failure of general protective/sensing circuits such as blackout detection or generator voltage regulator failures, etc.
| Other | All other equipment failures including discovery of design failures
| Relay | All relay failures, except relays for transformer or individual circuit breaker controls
| Transformer | Direct transformer failure or failure of transformer auxiliary equipment
G | Equip - other | Grid equipment failure
| Other - fire | Grid-centered fire
| Other - load | Grid power reduction (brownout)
HE | Maintenance | Errors by maintenance personnel that directly or indirectly caused an event
| Other | All other human errors
| Switching | Errors during electrical switching operations, not directly required by testing, generally involving breaker manipulation
| Testing | Errors by test personnel including errors while establishing or restoring from testing lineups including electrical distribution changes
HES | Maintenance | Errors by maintenance personnel that directly or indirectly caused an event
| Other | All other human errors
| Switching | Errors during electrical switching operations, not directly required by testing, generally involving breaker manipulation
| Testing | Errors by test personnel including errors while establishing or restoring from testing lineups including electrical distribution changes
Other | Mayflies | Mayflies
| Sabotage | Sabotage
SEE | Dust | Dust raised up by the wind
| Earthquake | Earthquake < 7.0 on the Richter Scale
| Fire | Fire
| Flooding | Flooding < 500-year flood for the site
| High Winds | High winds < 125 mph
| Ice | Ice
| Lightning | Lightning
| Rain | Rain
| Salt Spray | Salt spray
| Smoke | Smoke contamination
| Snow | Snow
| Snow and Wind | Combination of snow and wind

## LOOP Events 1987–2022
LER | Plant Name | Date | Operating Mode | LOOP Category | LOOP Class | Switchyard Restoration Time | Potential Bus Recovery Time | Actual Bus Restoration Time | Cause | Specific Cause
3132013001 | Arkansas 1 | 2013-03-31 | Shutdown | PC | LOOP-SD | unk. | 8640 | 8640 | HES | Other
3341993013 | Beaver Valley 1 | 1993-10-12 | Critical | SC | LOOP-IE-I | 15 | 28 | 28 | HES | Maintenance
4121987036 | Beaver Valley 2 | 1987-11-17 | Critical | SC | LOOP-IE-I | 0 | 4 | 4 | Equip | Breaker
3341993013 | Beaver Valley 2 | 1993-10-12 | Shutdown | SC | LOOP-SD | 15 | 28 | 28 | HES | Maintenance
1551992000 | Big Rock Point | 1992-01-29 | Shutdown | SC | LOOP-SD | 77 | 82 | 82 | Equip | Other
4561987048 | Braidwood 1 | 1987-09-11 | Shutdown | SC | LOOP-SD | 62 | 63 | 63 | Equip | Transformer
4561988022 | Braidwood 1 | 1988-10-16 | Critical | SC | LOOP-IE-I | 95 | 118 | 213 | Equip | Breaker
4561998003 | Braidwood 1 | 1998-09-06 | Shutdown | WR | LOOP-SD | 528 | 533 | 533 | SEE | High Winds
4572009002 | Braidwood 2 | 2009-07-30 | Critical | SC | LOOP-IE-I | 0.99996 | 2 | 3097 | Equip | Relay
2592011001 | Browns Ferry 1 | 2011-04-27 | Critical | WR | LOOP-IE-I | 0.99996 | 16 | 7414 | EEE | Tornado
2592011001 | Browns Ferry 2 | 2011-04-27 | Critical | WR | LOOP-IE-I | 0.99996 | 16 | 7414 | EEE | Tornado
2961997001 | Browns Ferry 3 | 1997-03-05 | Shutdown | SC | LOOP-SD | 39 | 44 | 44 | Equip | Transformer
2592011001 | Browns Ferry 3 | 2011-04-27 | Critical | WR | LOOP-IE-I | 0.99996 | 16 | 7414 | EEE | Tornado
2962012003 | Browns Ferry 3 | 2012-05-22 | Critical | SC | LOOP-IE-I | 86 | 91 | 101 | Equip | Relay
2962019001 | Browns Ferry 3 | 2019-03-09 | Critical | PC | LOOP-IE-NC | 60 | 62 | 781 | HE | Switching
3251993008 | Brunswick 1 | 1993-03-17 | Shutdown | WR | LOOP-SD | 1120 | 1125 | 1508 | SEE | Salt Spray
3252000001 | Brunswick 1 | 2000-03-03 | Shutdown | SC | LOOP-SD | 15 | 30 | 136 | HES | Testing
3252004002 | Brunswick 1 | 2004-08-14 | Critical | WR | LOOP-IE-I | 167 | 172 | 183 | EEE | Hurricane
3252016001 | Brunswick 1 | 2016-02-07 | Critical | PC | LOOP-IE-I | 0.99996 | 16 | 196 | Equip | Breaker
3252020003 | Brunswick 1 | 2020-08-03 | Critical | WR | LOOP-IE-I | 838 | 839 | 898 | EEE | Hurricane
3241989009 | Brunswick 2 | 1989-06-17 | Critical | SC | LOOP-IE-I | 85 | 90 | 403 | HE | Maintenance
3251993008 | Brunswick 2 | 1993-03-16 | Shutdown | WR | LOOP-SD | 813 | 818 | 1018 | SEE | Salt Spray
3241994008 | Brunswick 2 | 1994-05-21 | Shutdown | PC | LOOP-SD | 2 | 17 | 42 | HES | Testing
3242006001 | Brunswick 2 | 2006-11-01 | Critical | SC | LOOP-IE-I | 0.99996 | 16 | 1456 | Equip | Transformer
4541996007 | Byron 1 | 1996-05-23 | Shutdown | SC | LOOP-SD | 715 | 720 | 1763 | Equip | Transformer
4542014003 | Byron 1 | 2014-03-15 | Shutdown | SC | LOOP-SD | 613 | 613 | 613 | Equip | Transformer
4551987019 | Byron 2 | 1987-10-02 | Critical | SC | LOOP-IE-C | 0.99996 | 16 | 507 | HES | Switching
4542012001 | Byron 2 | 2012-01-30 | Critical | SC | LOOP-IE-I | 0.99996 | 2035 | 2172 | Equip | Transformer
3171987012 | Calvert Cliffs 1 | 1987-07-23 | Critical | SC | LOOP-IE-I | 113 | 118 | 118 | Equip | Circuits
3172015002 | Calvert Cliffs 1 | 2015-04-07 | Critical | GR | LOOP-IE-I | 200 | 210 | 210 | G | Equip - other
3171987012 | Calvert Cliffs 2 | 1987-07-23 | Critical | SC | LOOP-IE-I | 113 | 118 | 118 | Equip | Circuits
3172015002 | Calvert Cliffs 2 | 2015-04-07 | Critical | GR | LOOP-IE-NC | 19 | 29 | 29 | G | Equip - other
4132006001 | Catawba 1 | 2006-05-20 | Critical | SC | LOOP-IE-I | 385 | 400 | 542 | Equip | Circuits
4132012001 | Catawba 1 | 2012-04-04 | Critical | PC | LOOP-IE-C | 325 | 326 | 326 | Equip | Circuits
4141996001 | Catawba 2 | 1996-02-06 | Critical | SC | LOOP-IE-I | 115 | 120 | 330 | Equip | Transformer
4132006001 | Catawba 2 | 2006-05-20 | Critical | SC | LOOP-IE-I | 372 | 387 | 570 | Equip | Circuits
4132012001 | Catawba 2 | 2012-04-04 | Shutdown | SC | LOOP-SD | 60 | 61 | 393 | Equip | Circuits
4611999002 | Clinton 1 | 1999-01-06 | Shutdown | SC | LOOP-SD | 270 | 275 | 492 | Equip | Other
3971989016 | Columbia | 1989-05-14 | Shutdown | SC | LOOP-SD | 0 | 15 | 29 | HES | Maintenance
3151991004 | Cook 1 | 1991-05-12 | Critical | PC | LOOP-IE-I | 0 | 15 | 81 | Equip | Other
3021987025 | Crystal River 3 | 1987-10-16 | Shutdown | SC | LOOP-SD | 18 | 28 | 59 | HES | Maintenance
3021989023 | Crystal River 3 | 1989-06-16 | Critical | SC | LOOP-IE-I | 60 | 65 | 65 | HE | Testing
3021989025 | Crystal River 3 | 1989-06-29 | Shutdown | SC | LOOP-SD | 0 | 2 | 2 | SEE | Lightning
3021991010 | Crystal River 3 | 1991-10-20 | Shutdown | PC | LOOP-SD | 0 | 4 | 4 | HES | Other
3021992001 | Crystal River 3 | 1992-03-27 | Critical | PC | LOOP-IE-I | 20 | 30 | 150 | HE | Maintenance
3021993000 | Crystal River 3 | 1993-03-17 | Shutdown | WR | LOOP-SD | 72 | 77 | 102 | SEE | Salt Spray
3021993002 | Crystal River 3 | 1993-03-29 | Shutdown | WR | LOOP-SD | 0 | 15 | 37 | SEE | Flooding
3021993004 | Crystal River 3 | 1993-04-08 | Shutdown | PC | LOOP-SD | 0.99996 | 16 | 136 | HES | Maintenance
3461998006 | Davis-Besse | 1998-06-24 | Critical | WR | LOOP-IE-I | 1364 | 1428 | 1495 | EEE | Tornado
3462000004 | Davis-Besse | 2000-04-22 | Shutdown | PC | LOOP-SD | 5 | 10 | 10 | HES | Testing
3462003009 | Davis-Besse | 2003-08-14 | Shutdown | GR | LOOP-SD | 652 | 657 | 849 | G | Other - load
2751991004 | Diablo Canyon 1 | 1991-03-07 | Shutdown | SC | LOOP-SD | 261 | 285 | 285 | HES | Maintenance
2751995014 | Diablo Canyon 1 | 1995-10-21 | Shutdown | SC | LOOP-SD | 40 | 45 | 951 | HES | Maintenance
2752000004 | Diablo Canyon 1 | 2000-05-15 | Critical | PC | LOOP-IE-I | 1901 | 1906 | 2014 | Equip | Other
2752007001 | Diablo Canyon 1 | 2007-05-12 | Shutdown | GR | LOOP-SD | 209 | 245 | 279 | Equip | Other
3231988008 | Diablo Canyon 2 | 1988-07-17 | Critical | SC | LOOP-IE-I | 33 | 38 | 38 | Equip | Transformer
2371990002 | Dresden 2 | 1990-01-16 | Critical | SC | LOOP-IE-C | 0 | 45 | 759 | Equip | Transformer
2491989001 | Dresden 3 | 1989-03-25 | Critical | SC | LOOP-IE-I | 45 | 50 | 50 | Equip | Breaker
2492004003 | Dresden 3 | 2004-05-05 | Critical | SC | LOOP-IE-I | 146 | 151 | 151 | Equip | Breaker
3311990007 | Duane Arnold | 1990-07-09 | Shutdown | SC | LOOP-SD | 0 | 37 | 37 | HES | Testing
3312007004 | Duane Arnold | 2007-02-24 | Shutdown | WR | LOOP-SD | 5 | 1048 | 1829 | SEE | Ice
3312020001 | Duane Arnold | 2020-08-10 | Critical | WR | LOOP-IE-I | 1514 | 1515 | 1634 | EEE | Hurricane
3482000005 | Farley 1 | 2000-04-09 | Shutdown | SC | LOOP-SD | 18 | 19 | 19 | Equip | Relay
3412003002 | Fermi 2 | 2003-08-14 | Critical | GR | LOOP-IE-I | 379 | 384 | 582 | G | Other - load
3331988011 | FitzPatrick | 1988-10-31 | Shutdown | WR | LOOP-SD | 0.99996 | 16 | 70 | SEE | High Winds
3332003001 | FitzPatrick | 2003-08-14 | Critical | GR | LOOP-IE-I | 169 | 174 | 414 | G | Other - load
3332012005 | FitzPatrick | 2012-10-05 | Shutdown | SC | LOOP-SD | 847 | 847 | 847 | HE | Maintenance
2851987008 | Fort Calhoun | 1987-03-21 | Shutdown | SC | LOOP-SD | 37 | 38 | 38 | HES | Maintenance
2851987009 | Fort Calhoun | 1987-04-04 | Shutdown | SC | LOOP-SD | 0 | 4 | 4 | HES | Maintenance
2851990006 | Fort Calhoun | 1990-02-26 | Shutdown | SC | LOOP-SD | 0 | 14 | 14 | HES | Maintenance
2851998005 | Fort Calhoun | 1998-05-20 | Shutdown | SC | LOOP-SD | 104 | 109 | 109 | Equip | Transformer
2851999004 | Fort Calhoun | 1999-10-26 | Shutdown | PC | LOOP-SD | 2 | 2 | 2 | Equip | Other
2442003002 | Ginna | 2003-08-14 | Critical | GR | LOOP-IE-I | 49 | 54 | 297 | G | Other - load
4162003002 | Grand Gulf | 2003-04-24 | Critical | SC | LOOP-IE-NC | 0.99996 | 15 | 75 | SEE | High Winds
2131993009 | Haddam Neck | 1993-06-22 | Shutdown | PC | LOOP-SD | 12 | 27 | 35 | Equip | Circuits
2131993010 | Haddam Neck | 1993-06-26 | Shutdown | PC | LOOP-SD | 3 | 18 | 40 | Equip | Circuits
4002016005 | Harris | 2016-10-08 | Shutdown | WR | LOOP-SD | unk. | 443 | 524 | EEE | Hurricane
2471991006 | Indian Point 2 | 1991-03-20 | Shutdown | SC | LOOP-SD | 0 | 15 | 29 | Equip | Other
2471991010 | Indian Point 2 | 1991-06-22 | Shutdown | PC | LOOP-SD | 0 | 60 | 60 | Equip | Breaker
2471998013 | Indian Point 2 | 1998-09-01 | Shutdown | PC | LOOP-SD | 0.99996 | 16 | 67 | HES | Testing
2471999015 | Indian Point 2 | 1999-08-31 | Critical | SC | LOOP-IE-NC | 0.99996 | 15 | 779 | Equip | Circuits
2472003005 | Indian Point 2 | 2003-08-14 | Critical | GR | LOOP-IE-I | 97 | 102 | 214 | G | Other - load
2861995004 | Indian Point 3 | 1995-02-27 | Shutdown | SC | LOOP-SD | 30 | 40 | 132 | HES | Maintenance
2861996002 | Indian Point 3 | 1996-01-20 | Shutdown | SC | LOOP-SD | 30 | 40 | 145 | Equip | Transformer
2861997008 | Indian Point 3 | 1997-06-16 | Shutdown | GR | LOOP-SD | 37 | 42 | 42 | HE | Maintenance
2862003005 | Indian Point 3 | 2003-08-14 | Critical | GR | LOOP-IE-I | 97 | 102 | 241 | G | Other - load
3731993015 | La Salle 1 | 1993-09-14 | Critical | SC | LOOP-IE-I | 0 | 15 | 70 | Equip | Transformer
3732013002 | La Salle 1 | 2013-04-17 | Critical | SC | LOOP-IE-NC | 481 | 481 | 482 | SEE | Lightning
3732013002 | La Salle 2 | 2013-04-17 | Critical | SC | LOOP-IE-NC | 481 | 481 | 482 | SEE | Lightning
3091988006 | Maine Yankee | 1988-08-13 | Critical | SC | LOOP-IE-I | 14 | 15 | 15 | Equip | Transformer
3691987021 | McGuire 1 | 1987-09-16 | Shutdown | PC | LOOP-SD | 0 | 6 | 6 | HES | Testing
3691991001 | McGuire 1 | 1991-02-11 | Critical | PC | LOOP-IE-I | 0 | 40 | 60 | HE | Testing
3691988014 | McGuire 2 | 1988-06-24 | Shutdown | SC | LOOP-SD | 8 | 8 | 8 | HES | Switching
3701993008 | McGuire 2 | 1993-12-27 | Critical | SC | LOOP-IE-I | 96 | 101 | 131 | Equip | Transformer
2451989012 | Millstone 1 | 1989-04-29 | Shutdown | SC | LOOP-SD | 0 | 15 | 75 | HES | Other
3361988011 | Millstone 2 | 1988-10-25 | Critical | PC | LOOP-IE-I | 19 | 29 | 29 | HE | Maintenance
3362008004 | Millstone 2 | 2008-05-24 | Shutdown | SC | LOOP-SD | 57 | 57 | 1612 | G | Equip - other
3362014006 | Millstone 2 | 2014-05-25 | Critical | GR | LOOP-IE-NC | 179 | 184 | 209 | Equip | Other
4232007002 | Millstone 3 | 2007-04-25 | Shutdown | GR | LOOP-SD | 133 | 193 | 220 | HES | Switching
3362014006 | Millstone 3 | 2014-05-25 | Critical | GR | LOOP-IE-NC | 179 | 184 | 209 | Equip | Other
2202003002 | Nine Mile Pt. 1 | 2003-08-14 | Critical | GR | LOOP-IE-NC | 105 | 110 | 448 | G | Other - load
4101988062 | Nine Mile Pt. 2 | 1988-12-26 | Shutdown | SC | LOOP-SD | 9 | 24 | 54 | Equip | Transformer
4101992006 | Nine Mile Pt. 2 | 1992-03-23 | Shutdown | PC | LOOP-SD | 20 | 30 | 50 | HES | Maintenance
4102003002 | Nine Mile Pt. 2 | 2003-08-14 | Critical | GR | LOOP-IE-I | 100 | 105 | 551 | G | Other - load
3382011003 | North Anna 1 | 2011-08-23 | Critical | SC | LOOP-IE-NC | 467 | 547 | 547 | SEE | Earthquake
3382011003 | North Anna 2 | 2011-08-23 | Critical | SC | LOOP-IE-NC | 467 | 547 | 547 | SEE | Earthquake
2701992004 | Oconee 2 | 1992-10-19 | Critical | PC | LOOP-IE-I | 207 | 207 | 207 | HE | Maintenance
2871987002 | Oconee 3 | 1987-03-05 | Shutdown | SC | LOOP-SD | 150 | 155 | 155 | HES | Maintenance
2872006001 | Oconee 3 | 2006-05-15 | Shutdown | PC | LOOP-SD | 606 | 606 | 1730 | HES | Maintenance
2872018002 | Oconee 3 | 2018-05-10 | Shutdown | PC | LOOP-SD | 807 | 807 | 807 | Equip | Relay
2191989015 | Oyster Creek | 1989-05-18 | Critical | PC | LOOP-IE-I | 0.99996 | 16 | 54 | HE | Maintenance
2191992005 | Oyster Creek | 1992-05-03 | Critical | GR | LOOP-IE-I | 5 | 65 | 1029 | SEE | Fire
2191997010 | Oyster Creek | 1997-08-01 | Critical | SC | LOOP-IE-C | 30 | 40 | 40 | Equip | Relay
2192009005 | Oyster Creek | 2009-07-12 | Critical | GR | LOOP-IE-I | 94 | 103 | 103 | SEE | Lightning
2192012001 | Oyster Creek | 2012-07-23 | Critical | GR | LOOP-IE-I | 0.99996 | 31 | 88 | Equip | Relay
2192012002 | Oyster Creek | 2012-10-29 | Shutdown | WR | LOOP-SD | 861 | 861 | 861 | SEE | High Winds
2551987024 | Palisades | 1987-07-14 | Critical | SC | LOOP-IE-I | 388 | 388 | 446 | HE | Maintenance
2551992032 | Palisades | 1992-04-06 | Shutdown | PC | LOOP-SD | 0 | 15 | 30 | HES | Testing
2551998013 | Palisades | 1998-12-22 | Shutdown | PC | LOOP-SD | 0.99996 | 16 | 20 | Equip | Transformer
2552003003 | Palisades | 2003-03-25 | Shutdown | PC | LOOP-SD | 91 | 96 | 3261 | HES | Maintenance
5282004006 | Palo Verde 1 | 2004-06-14 | Critical | GR | LOOP-IE-I | 32 | 37 | 57 | G | Equip - other
5282004006 | Palo Verde 2 | 2004-06-14 | Critical | GR | LOOP-IE-I | 32 | 37 | 106 | G | Equip - other
5282004006 | Palo Verde 3 | 2004-06-14 | Critical | GR | LOOP-IE-I | 32 | 37 | 59 | G | Equip - other
2771988020 | Peach Bottom 2 | 1988-07-29 | Shutdown | SC | LOOP-SD | 9 | 24 | 125 | Equip | Transformer
2772003004 | Peach Bottom 2 | 2003-09-15 | Critical | GR | LOOP-IE-I | 0.99996 | 16 | 41 | Equip | Relay
2771988020 | Peach Bottom 3 | 1988-07-29 | Shutdown | SC | LOOP-SD | 9 | 24 | 125 | Equip | Transformer
2772003004 | Peach Bottom 3 | 2003-09-15 | Critical | GR | LOOP-IE-I | 0.99996 | 16 | 103 | Equip | Relay
4402003002 | Perry | 2003-08-14 | Critical | GR | LOOP-IE-I | 82 | 87 | 123 | G | Other - load
2931987005 | Pilgrim | 1987-03-31 | Shutdown | WR | LOOP-SD | 0.99996 | 16 | 45 | SEE | High Winds
2931987014 | Pilgrim | 1987-11-12 | Shutdown | WR | LOOP-SD | 1258 | 1263 | 1263 | SEE | Salt Spray
2931989010 | Pilgrim | 1989-02-21 | Shutdown | SC | LOOP-SD | 0.99996 | 16 | 920 | Equip | Other
2931991024 | Pilgrim | 1991-10-30 | Decay Heat | WR | LOOP-SD | 109 | 114 | 152 | SEE | Salt Spray
2931993004 | Pilgrim | 1993-03-13 | Critical | WR | LOOP-IE-I | 30 | 40 | 298 | SEE | Snow
2931993010 | Pilgrim | 1993-05-19 | Shutdown | SC | LOOP-SD | 36 | 37 | 37 | HES | Testing
2931993022 | Pilgrim | 1993-09-10 | Critical | SC | LOOP-IE-I | 10 | 25 | 200 | SEE | Lightning
2931997007 | Pilgrim | 1997-04-01 | Shutdown | WR | LOOP-SD | 347 | 1200 | 1409 | SEE | High Winds
2932008007 | Pilgrim | 2008-12-20 | Shutdown | SC | LOOP-SD | 2 | 60 | 120 | SEE | Ice
2932013003 | Pilgrim | 2013-02-08 | Critical | WR | LOOP-IE-I | 656 | 1258 | 1843 | SEE | Snow and Wind
2932013003 | Pilgrim | 2013-02-10 | Shutdown | SC | LOOP-SD | 2271 | 2387 | 3333 | SEE | Ice
2932013009 | Pilgrim | 2013-10-14 | Critical | GR | LOOP-IE-I | 0.99996 | 2 | 1382 | G | Equip - other
2932015001 | Pilgrim | 2015-01-27 | Critical | WR | LOOP-IE-I | 0.99996 | 2 | 3641 | SEE | Snow and Wind
2932018004 | Pilgrim | 2018-03-13 | Shutdown | WR | LOOP-SD | 720 | 721 | 4018 | SEE | Snow and Wind
2661992003 | Point Beach 1 | 1992-04-28 | Shutdown | PC | LOOP-SD | 0 | 15 | 30 | HES | Maintenance
2662011001 | Point Beach 1 | 2011-11-27 | Shutdown | SC | LOOP-SD | 0.99996 | 16 | 334 | Equip | Other
3011989002 | Point Beach 2 | 1989-03-29 | Critical | SC | LOOP-IE-C | 90 | 95 | 202 | HE | Maintenance
2661994010 | Point Beach 2 | 1994-09-27 | Shutdown | PC | LOOP-SD | 0 | 15 | 15 | HES | Switching
2821996012 | Prairie Island 1 | 1996-06-29 | Critical | WR | LOOP-IE-I | 296 | 301 | 301 | SEE | High Winds
2821996012 | Prairie Island 2 | 1996-06-29 | Critical | WR | LOOP-IE-I | 296 | 301 | 301 | SEE | High Winds
2651991005 | Quad Cities 1 | 1991-04-02 | Shutdown | PC | LOOP-SD | unk. | unk. | unk. | Equip | Transformer
2651992011 | Quad Cities 2 | 1992-04-02 | Shutdown | PC | LOOP-SD | 35 | 35 | 35 | Equip | Transformer
2652001001 | Quad Cities 2 | 2001-08-02 | Critical | SC | LOOP-IE-I | 15 | 30 | 154 | SEE | Lightning
2611992017 | Robinson 2 | 1992-08-22 | Critical | SC | LOOP-IE-I | 454 | 459 | 914 | Equip | Transformer
2612016005 | Robinson 2 | 2016-10-08 | Critical | SC | LOOP-IE-I | 0.99996 | 621 | 621 | G | Equip - other
2722003002 | Salem 1 | 2003-07-29 | Critical | SC | LOOP-IE-I | 30 | 40 | 480 | Equip | Circuits
3111994014 | Salem 2 | 1994-11-18 | Shutdown | SC | LOOP-SD | 295 | 300 | 1675 | Equip | Relay
3622002001 | San Onofre 3 | 2002-02-27 | Critical | SC | LOOP-IE-I | 32 | 32 | 32 | HE | Testing
4431988004 | Seabrook | 1988-08-10 | Shutdown | PC | LOOP-SD | 4 | 5 | 5 | HES | Switching
4431991008 | Seabrook | 1991-06-27 | Critical | SC | LOOP-IE-I | 0 | 20 | 20 | Equip | Relay
4432001002 | Seabrook | 2001-03-05 | Critical | WR | LOOP-IE-I | 0.99996 | 16 | 2122 | SEE | Snow
3271992027 | Sequoyah 1 | 1992-12-31 | Critical | SC | LOOP-IE-I | 96 | 101 | 116 | Equip | Breaker
3271997007 | Sequoyah 1 | 1997-04-04 | Shutdown | PC | LOOP-SD | 325 | 330 | 345 | HE | Maintenance
3271992027 | Sequoyah 2 | 1992-12-31 | Critical | SC | LOOP-IE-I | 96 | 101 | 116 | Equip | Breaker
3352004004 | St. Lucie 1 | 2004-09-25 | Shutdown | WR | LOOP-SD | 8 | 68 | 667 | EEE | Hurricane
3352016003 | St. Lucie 1 | 2016-08-21 | Critical | PC | LOOP-IE-NC | 0.99996 | 70 | 70 | Equip | Circuits
3352004004 | St. Lucie 2 | 2004-09-25 | Shutdown | WR | LOOP-SD | 8 | 68 | 613 | EEE | Hurricane
3951989012 | Summer | 1989-07-11 | Critical | PC | LOOP-IE-C | 95 | 100 | 120 | G | Equip - other
2802011001 | Surry 1 | 2011-04-16 | Critical | WR | LOOP-IE-I | 303 | 304 | 346 | EEE | Tornado
2802011001 | Surry 2 | 2011-04-16 | Critical | WR | LOOP-IE-I | 303 | 304 | 424 | EEE | Tornado
2891997007 | Three Mile Isl 1 | 1997-06-21 | Critical | SC | LOOP-IE-I | 85 | 90 | 90 | Equip | Circuits
2501991003 | Turkey Point 3 | 1991-07-24 | Shutdown | SC | LOOP-SD | 0 | 11 | 11 | Equip | Breaker
2501992000 | Turkey Point 3 | 1992-08-24 | Shutdown | WR | LOOP-SD | 7950 | 7955 | 9221 | EEE | Hurricane
2511991001 | Turkey Point 4 | 1991-03-13 | Shutdown | PC | LOOP-SD | 62 | 67 | 67 | Equip | Relay
2501992000 | Turkey Point 4 | 1992-08-24 | Shutdown | WR | LOOP-SD | 7908 | 7913 | 9442 | EEE | Hurricane
2512000004 | Turkey Point 4 | 2000-10-21 | Shutdown | SC | LOOP-SD | 0.99996 | 16 | 111 | Equip | Circuits
2512005005 | Turkey Point 4 | 2005-10-31 | Shutdown | WR | LOOP-SD | 0.99996 | 1598 | 1615 | SEE | Salt Spray
2512013002 | Turkey Point 4 | 2013-04-19 | Critical | PC | LOOP-IE-NC | 24 | 27 | 30 | HE | Testing
2711987008 | Vermont Yankee | 1987-08-17 | Shutdown | GR | LOOP-SD | 2 | 17 | 77 | Equip | Other
2711991009 | Vermont Yankee | 1991-04-23 | Critical | PC | LOOP-IE-I | 277 | 282 | 822 | HE | Maintenance
4241990006 | Vogtle 1 | 1990-03-20 | Shutdown | SC | LOOP-SD | 140 | 145 | 217 | HES | Other
3822005004 | Waterford 3 | 2005-08-29 | Shutdown | WR | LOOP-SD | 4981 | 4982 | 5242 | EEE | Hurricane
3822017002 | Waterford 3 | 2017-07-17 | Critical | PC | LOOP-IE-I | 145 | 158 | 158 | Equip | Relay
3822021002 | Waterford 3 | 2021-08-29 | Decay Heat | WR | LOOP-SD | 3206 | 3211 | 3211 | EEE | Hurricane
4821987048 | Wolf Creek | 1987-10-14 | Shutdown | PC | LOOP-SD | 0 | 17 | 17 | HES | Maintenance
4822008004 | Wolf Creek | 2008-04-07 | Shutdown | SC | LOOP-SD | 7 | 7 | 153 | HES | Maintenance
4822009002 | Wolf Creek | 2009-08-19 | Critical | WR | LOOP-IE-I | 0.99996 | 133 | 133 | SEE | Lightning
4822012001 | Wolf Creek | 2012-01-13 | Critical | SC | LOOP-IE-I | 177 | 177 | 198 | Equip | Breaker
291991002 | Yankee-Rowe | 1991-06-15 | Critical | SC | LOOP-IE-I | 24 | 25 | 25 | SEE | Lightning
2951997007 | Zion 1 | 1997-03-11 | Shutdown | SC | LOOP-SD | 235 | 240 | 240 | Equip | Circuits
3041991002 | Zion 2 | 1991-03-21 | Critical | SC | LOOP-IE-I | 0 | 60 | 60 | Equip | Transformer